Access Control System Specification

Overview

The Access Central Access Control System specified herein shall be manufactured by Toye Corporation of Chatsworth California.

Instrumental to this specification are the following key design elements from which no substitution or omission may be made:

UL 294 Certification

All card readers and field modules shall be UL 294 listed.

Real Time Central Control

Programming and event management must be subject to instantaneous control and monitoring from one or more PC’s connected directly, or via a LAN or WAN network. Uploading or downloading from remote panels is not acceptable unless it is from a remote location accessible only by dial-up.

Full 100% high security shall not be compromised by a PC failure, or a complete shut down of any LAN or WAN network.

Open Architecture Software

The access control system shall use the standard unmodified commercial version of Microsoft Access version 7 or higher for cardholder and event management. All special tables, queries, macros, reports, and code modules shall be open and available to users who wish to customize their systems in order to utilize the full potential of Microsoft Access. Proprietary software is not acceptable.

Event Management

Any connected PC shall be capable of uniquely annunciating each incoming cardholder or alarm event:

Instantly display a photograph of the person entering

Assign a sound file to each event uniquely

Trigger a remote relay for certain transactions

Send an instant cell phone text message describing the particular event

Send an instant e-mail describing the particular event

Display a unique graphic file for each and every event

Display a list of open alarms

Display a list of Who’s In

Display a list of Who’s Out

Designate any incoming event to switch all programming parameters to an emergency mode

Event Management shall be a stand-alone software package, which can be configured differently, as needed on each LAN workstation

Time and Attendance

It shall be possible to generate reports based on the amount of time cardholders are in a facility, and it shall be possible to create the reports based on any time period such as daily, weekly, or monthly. It shall be possible to create reports by individuals, or individuals within groups with totals based on individuals or groups.

The software shall permit the user to produce reports, which shall include the following: System activity by location, time, cardholder, or transaction status.

Network Controllers with Distributed Processing

The system shall be based on independent stand-alone Network Controllers, each capable of controlling 127 readers, 2000 alarm points, and 65,000 cardholders. The Network Controllers shall be equipped with a 10/100-network card and be fully compatible with standard LAN or WAN networks.

Independent Entry Points

Each entry point card reader shall be controlled by a Remote Command Module, which shall be connected to a two pair wiring network terminating at a Network Controller. The Remote Command Module shall be capable of granting access in the event the Network Controller fails, or there is a fault in the wiring network.

Access Card Media Technology

The system shall be capable of supporting the following reading technologies:

All Proximity formats

Bar Code

Magnetic stripe

Smart Card

Wiegand

Touch

Barium Ferrite

Vehicle I.D: HID, AutoAccess, Radio Key, Laser Data, Smart Pass, Sirit

Any technology supporting Wiegand, RS-232 or RS-422 data output.

Keypad access with or without associated readers.

Field Communication Wiring

The Access Control System shall consist of a single common 2 pair communication trunk capable of supporting all system devices required for building security, alarm monitoring, elevator control, parking access, space counting, and vehicle I.D.

Network Controller

The heart of the systems hardware architecture is the miniature Network Controller. It shall be a stand-alone access controller capable of real-time control form a single PC, or from a network of PCs. The Network Controller shall be contain a Pentium level compatible microcomputer, and shall have sufficient memory for 65,000 cardholders, 127 entry points, 2000 alarms, and transaction storage for a minimum of 100,000 transactions.

Software Features

The Microsoft Access based Access Anywhere head end software shall be capable of the following:

Management and control of any number of Network Controller based subsystems

Password Management and log on report generation

Digital Photo ID card production

Full report generation

Keypad programming, which shall determine when access shall be granted, based on card only, card and Keypad code, or keypad code only

Supervisor First Option shall not allow access to individuals otherwise valid for entry unless a supervisor’s card was first used.

# Parking Management

The system shall provide user selectable "hard" or "soft" anti-pass-back on exits only, entrances only, or both.

The system shall provide levels of exception for specific cardholders not subject to anti-pass-back control.

The system shall support Tenant Specific Space Allocation allowing a pre-designated number of open parking spaces for each tenant.

The system shall provide for car pool access control.

The system shall provide for hard or soft "Nesting" control to force parkers into specific areas. A user selectable "grace time" shall be provided.

The system shall provide Pre-Pay (Pay On Foot) cashiering with a user selectable exit grace period.

The Access Control software shall provide for an optional card use-debiting feature by dollar amount or by number of uses.

The system shall provide real time space counting with the ability to display the status of up to 64 counters.

Each counter must provide inputs for 12 up counts, and/or 12 down counts. Each counter must provide up to 12 zero count outputs for controlling lot full signs and ticket spitter inhibit. A setup screen shall be provided to enable the user to define and identify each counter with up to 48 characters of text.

Definable counters shall include:

1. Number of vehicles presently in any lot

2. Spaces available in any lot

3. Cumulative total entries by entry point

4. Cumulative total exits by exit point

5. Cumulative grand total

6. Number of Tickets dispensed

7. Number of monthlies in any lot

8. Non resettable counters

9. Cash drawer operations

10. All counter transaction data shall be stored to the hard disk for future status viewing and reports. It shall be possible at a later date to view and/or print out the status of any counter.

11. The system shall produce a counter report on demand recapping the prior 24-hour period showing all count statistics on an hour-by-hour basis with totalizing at the bottom. Maximum occupancy during any period, or maximum spaces available during any period shall be reported.

Special Parking Management Software

Hotel Guest Parking

This feature shall allow a clerk to enable guest parking for a 24 hour period based on the guest’s parking ticket. The ticket shall automatically expire unless programmed for an extended period.

Tenant Billing

For parking operators requiring automatic monthly billing of tenants, it shall be possible to generate invoices showing one or more cardholders assigned to that tenant, variable rates for each cardholder within a tenant group, extra services, and applicable local taxes.

The system shall provide for positive posting of payments, which shall automatically enable all cardholders as a group, or deactivate all cardholders as a group for non-payment.

A tenant group may consist of a single cardholder, or a group of cardholders, and there shall be no limit to the number of groups or individual cardholders.

Time Management

It shall be possible to generate reports based on the amount of time cardholders utilize a parking facility, and it shall be possible to create the reports based on any time period such as daily, weekly, or monthly. The time calculation shall include the ability to round up to the nearest half hour to create a basis for tenant billing. It shall be possible to create reports by individuals, or individuals within tenant groups with totals based on group totals.

The software shall permit the user to produce reports, which shall include the following: System activity by location, time, cardholder, or transaction status.

# VIP Tracking

The system shall provide an instantaneous real time list or "who's in" and/or “who’s out” for doctors or for V.I.P. Tracking, providing a dynamic display of selected cardholders who are presently on site. The display shall be in alphabetic order, and shall repaint any time a card being tracked enters or exits.

# CPU Redundancy

It shall be possible to constantly monitor the access control system form other PC's so that if for any reason the main PC fails, a backup will automatically take over full system functionality. The backup PC shall not be required to be dedicated to this use, and shall be fully available for use with other software programs while monitoring the access control system at the same time. When the main PC is back on line, the system shall switch back automatically.

# Programmable Input and Output Linking and Control

The system shall be capable of controlling up to 1600 separately programmable output relays for timed events or for momentary activation in response to valid card insertions, or alarm inputs.

# Alarm Monitoring

The system shall be capable of monitoring up to 2000 alarm points, and each alarm point shall be programmable as to shunt periods, and with appropriate unique text descriptions, which shall be, displayed in the transactions logs.

It shall be possible to program any incoming alarm to execute a BATch file that the system must carry out in response to that alarm such as to display a graphic or notify a pocket pager.

# Remote Dial Up Access and Programming

It shall be possible to use dial up modems to communicate with systems at remote locations. The operator at the host site shall be able to perform all the normal system functions including updating and data transfer.

Elevator Control

The software shall manage floor programmable control of each access card. It shall be possible to restrict access to any floor or combination of floors, based on day and time. The software must allow discretionary public access to specific floors, and secure access to other floors at the same time. Options to log actual cardholder floor selection must be available. In addition, optional configurations to limit one card transaction per floor selection shall also be available.

Smart Cartridges

The system shall optionally accommodate "Smart Cartridges" which can be used to provide off-site control of one of more readers or elevators.

It shall be possible to program cards in or out of the Smart Cartridge using any of the following techniques:

Connection to a PC

Card Programming Deck

Dial up from a remote PC.

Automatic Mass Unattended Programming of one or more remote sites via dial up

The cartridge shall contain program memory for the readers served, and shall be capable of storing up to 10,000 transactions should the PC go off-line. One Smart Cartridge shall be capable of backing-up the entire system.

During Smart Cartridge control, there shall be no degraded mode. The cardholder level programming, reader and time zone assignments shall be fully operational just as it would when controlled by the computer.

Should the Smart Cartridge take over control of the system in the event of a PC failure, the PC shall automatically resume control when restored.

Entry Point Components

Each entry point shall be controlled by Command Module. The Command Module shall be optionally configurable to accept two readers, and/or a keypad. The Command Module shall contain two Form C time programmable output relays, and two dry contact alarm inputs.

Software Memory Structure and Standard Features

The system shall provide for access level programming which shall consist of the following parameters:

One or more reader locations.

A start and end time

One of more days of the week

Holiday exceptions.

Start date and stop date option

At least 100 security levels shall be provided for cardholders.

At least 200 command levels shall be provided for reader shunt and unlock commands, and programmable output relays.

At least 32 user-defined holidays shall be programmable for security and command levels.

The system shall automatically adjust the system clock for daylight savings time changes.

The system shall permit both automatic alarm override, and automatic door unlock according to programmed parameters.

The system shall provide a keyboard command to raise any gate or open any door instantly.

The system shall provide a hard copy transaction log showing day, date, time, location, access status, card number, and customer assignable text.

The system shall provide a choice of printing all transactions, or just exceptions.

The system shall store all transactions to hard disk, and shall be capable of recalling past transactions according to any criteria.

The system shall provide an instant listing of cardholder programming assignments.

The system shall permit on-going monitoring of system activity on the video monitor.

Photo ID Imaging/Pop-up Photo Display

The Access Central Software shall support the creation of digital photo I.D. cards. It shall be possible to utilize an ordinary off-the-shelf digital camera. Photos that are downloaded onto the PC's hard drive may then be linked to the cardholder's record. The linked photo may then be used for photo badge creation, and/or for instant pop-up display (if option is enabled) when the card is used to gain entry.

Experience

The system to be installed shall be stock and off-the-shelf. It shall be produced by a manufacturer with a minimum of 25 years experience in computer based access control systems, and the specific system proposed as well as each required feature shall have been in full production for not less than one year.